## Info
Inputs to Power Performance validation
First column will be the name in the structure. | Second column will be the value assigned to the substructure | Third column is for comments not loaded to matlab
WTGStart |  | Start of WTG structure
CutInWSP | 3
CutOutWSP | 24
NomSpeed | 9.33
per85WSP | 10 | Wind speed at which 85% of Prated is reached
Lifetime | 20
RotorDiameter | 162
Vavg | 9.36
TIClass | 3 | Turbulence intensity, 1= A, 2 =B, 3 = C
Weibull | 2.16 | Weibull k-factor
WSBinSize | 0.5
TIBinSize | 2
TI_PlotLims | 3 13
TIQuantileBinSize | 10
ShearBinSize | 0.1
WDir_PlotLims | 225 315
Shear_PlotLims | .09 0.61
RhoRef | 1.225 | kg/m3
Rho_PlotLims | 1.1 1.3
Power | 6000
GenSpeed | 408
BldSNSlope | 10
TwrSNSlope | 4
MShaftSNSlope | 8
OthrSNSlope | 4
igear | 43.75
SC_WS | 3 5 6 12 31
SC_PC | 10 5 2 0.2
Trend_lim | 0.1
Trend_lim_amp | 0.2
MM_Nacelle_Diff | 5 | Percentage
WTGEnd |  | End of WTG structure
ReportStart |  | Start of Report Structure
date | 2021-10-05
WTG | EV162 Vidar 6MW
Site | Prototype at Oesterild pad4, Denmark
author | MACVL
reviewer
approver
IECclass | IECS
BladeType | Structural shell V162 blades
HubHeight | HH154 | Height of the tower
bldRoot | 2.5 | Distance at which root sensor is placed
MainShaft | NA | Distance from hub flange main shaft sensor is placed
TowerTop | NA | Height tower top sensor is placed
TowerMid | NA | Height tower mid sensor is placed
TowerBot | NA | Height tower bottom sensor is placed
IDNumber | 237525 | ID of the turbine
Controller | 2020.16.36 | VMPGlobal
VTSversion | VTS002v05_180
BladeMass | 1.0018 / 0.9968 / 1.0013;
AeroImbalance | -0.1/0.0/0.1
ReportEnd |  | End of Report Structure

## Sorting
Shorthand-name | Name in sensorlist | Comments (not loaded to Matlab)
START_SORTINGSENSORS
PitchA | PitchA | Pitch angle - Blade A
PitchB | PitchB | Pitch angle - Blade B
PitchC | PitchC | Pitch angle - Blade C
run | RUN | Turbine Operational State
Yerr | YawErr | Yaw error (YawExt-WDmHH)
Pow | Pow | Power - (Active Grid Power)
WSP | WSmR154 | MM - Wind speed - HH - 130m - Risø
Wak | YawCtrl | Yaw angle - Controller (north = 0deg) |  |  | Height (abs) | Height (rel) | 1Hz signals |  |  |  | TI
wdir | WDm150 | Wind dir - Near HH (150.28m) |  | 73 | 88 | -66 | PHWSH01 | 291 | PWYMH01 | 292 | SATIH01 | 242
temp | Temp150 | MM - Air temperature - near HH |  |  | 99 | -55 | PHWSH02 | 293 | PWYMH02 | 294 | SATIH02 | 246
pres | Pres150 | MM - Air pressure near HH |  |  | 110 | -44 | PHWSH03 | 295 | PWYMH03 | 296 | SATIH03 | 250
hum | Hum150 | MM - Humidity - near HH |  |  | 121 | -33 | PHWSH04 | 297 | PWYMH04 | 298 | SATIH04 | 254
Lidar_WSP | PHWSH07 | Lidar WS measurement at HH |  |  | 132 | -22 | PHWSH05 | 299 | PWYMH05 | 300 | SATIH05 | 258
Lidar_REWS | REWS | Lidar REWS |  |  | 143 | -11 | PHWSH06 | 301 | PWYMH06 | 302 | SATIH06 | 262
Lidar_TI | SATIH07 | Lidar TI at HH |  |  | 154 | 0 | PHWSH07 | 303 | PWYMH07 | 304 | SATIH07 | 266
PHWS | 313 313 311 309 307 305 303 301 299 297 295 295 |  |  |  | 165 | 11 | PHWSH08 | 305 | PWYMH08 | 306 | SATIH08 | 270
PHWS_Height | 236 209 198 187 176 165 154 143 132 121 110 72 |  |  |  | 176 | 22 | PHWSH09 | 307 | PWYMH09 | 308 | SATIH09 | 274
SATI | 250 250 254 258 262 266 270 274 278 282 286 286 |  |  |  | 187 | 33 | PHWSH10 | 309 | PWYMH10 | 310 | SATIH10 | 278
SATI_Height | -82 -44 -33 -22 -11 0 11 22 33 44 55 82 |  |  |  | 198 | 44 | PHWSH11 | 311 | PWYMH11 | 312 | SATIH11 | 282
Lidar_WD | PWYMH07 | Lidar WD at HH |  |  | 209 | 55 | PHWSH12 | 313 | PWYMH12 | 314 | SATIH12 | 286
PWYM | 296 296 298 300 302 304 306 308 310 312 314 314 |  |  | 235 | 220 | 66 | PHWSH13 | 315 | PWYMH13 | 316 | SATIH13 | 290
PWYM_Height | -82 -44 -33 -22 -11 0 11 22 33 44 55 82
WSC | WSnCtrl | Controlling Wind Speed Measured
WSN | WSnMeas | Nacelle Wind Speed
wsh | 1 4 5 | Numbers for wind sensors for Wshear calculation
wshHeight | 154 113 73 | Height for the wind sensors
rpm | Rotspd | Rotor speed
grpm | Grpm | Generator speed sensor
GenGrid | GenGrid | Generator Index. 0=NoGen 1=Delta 2=Star
WShear | 0 | Added later, dummy value of 0
turb | 0 | Added later, dummy value of 0
rho | 0 | Added later, dummy value of 0
Pstat | Pstat | Power production status
date | mDD | Measurement date, dummy
END_SORTINGSENSORS
Sorting table loaded into Matlab. Variable names should be same as shorthand-name above
Variable name | Parameter to sort on | Minimum value | Maximum value
Start_SortTable
date | filename_long | V162_20210327_0840 | V162_20210425_1650
End_SortTable

## Sensors
Desription | Simulation sens | Measurement sens | Sens. No
START_SENSORLIST
Wind speed (m/s) | Vhub | PHWSH07 | 1
Electrical power (kW) | P | PowA | 2
Rotor speed (rpm) | Omega | Rotspd | 3
Generator speed (rpm) | OmGen | Grpm | 4
BldC Pitch angle (deg) | Pi2 | PitchC | 5
BldA Pitch angle (deg) | Pi1 | PitchA | 6
BldB Pitch angle (deg) | Pi3 | PitchB | 7
Nacelle wind speed (m/s) | Vhub | WSnCtrl | 8
Wind Direction (deg) | Wdir | WDm150 | 9 | (For additional investigation)
END_SENSORLIST
START_GROUPING
Control_PwRpmPiAll | 2 3 4 5 6 7
Bldrt_flpAll_edgAll
Bld_otherSection
Ms_TYrotating
Ms_TYfixed_Trq
TwrTop_Tor_long_lat
TwrBase_Tor_long_lat
Twr_otherSection
OtherSensors | 5 6 7
END_GROUPING

## PowerCurveRef
Power, mode 0. (kW) HWO disabled |  | Third column with (power/power_rated) not loaded to matlab
| Air density(kg/m³) | P_rated (kW)
Wind(m/s) | 1.225 | 6000
Data_Start
3 | 32 | 0.0053333
3.5 | 150 | 0.025
4 | 292 | 0.048667
4.5 | 467 | 0.077833
5 | 676 | 0.11267
5.5 | 927 | 0.1545
6 | 1229 | 0.20483
6.5 | 1584 | 0.264
7 | 2000 | 0.33333
7.5 | 2476 | 0.41267
8 | 3017 | 0.50283
8.5 | 3624 | 0.604
9 | 4264 | 0.71067
9.5 | 4859 | 0.80983
10 | 5380 | 0.89667
10.5 | 5734 | 0.95567
11 | 5932 | 0.98867
11.5 | 5983 | 0.99717
12 | 5998 | 0.99967
12.5 | 6000 | 1
13 | 6000 | 1
13.5 | 6000 | 1
14 | 6000 | 1
14.5 | 6000 | 1
15 | 6000 | 1
15.5 | 6000 | 1
16 | 6000 | 1
16.5 | 6000 | 1
17 | 6000 | 1
17.5 | 6000 | 1
18 | 5846 | 0.97433
18.5 | 5581 | 0.93017
19 | 5360 | 0.89333
19.5 | 5128 | 0.85467
20 | 4844 | 0.80733
20.5 | 4555 | 0.75917
21 | 4268 | 0.71133
21.5 | 3985 | 0.66417
22 | 3690 | 0.615
22.5 | 3383 | 0.56383
23 | 3102 | 0.517
23.5 | 2801 | 0.46683
24 | 2479 | 0.41317
Data_End